## Slide 1: Portable Extinguishers Firefighter I
North Carolina Fire & Rescue Commission
Portable Extinguishers

## Slide 2: Lesson One Firefighter I
TERMINAL OBJECTIVE
The Firefighter I candidate shall identify in writing the classifications of fire as they relate to the use of fire extinguishers, define the fire extinguisher rating systems, identify the appropriate extinguisher and application procedures, and correctly demonstrate extinguishing Class A and B fires by using appropriate portable fire extinguishers.

## Slide 3: Enabling Objectives
The Firefighter I candidate, when given a fire scenario, shall correctly identify each of the five classes of fire and the appropriate type of fire extinguisher to use on each class.
The Firefighter I candidate shall correctly identify, verbally and in writing, the ratings of any given portable fire extinguisher.

## Slide 4: Enabling Objectives
The Firefighter I candidate shall correctly identify, verbally and in writing, the different types of fire extinguishers and the agents used in each.

## Slide 5: Enabling Objectives
The Firefighter I candidate shall visually, verbally, and by physical demonstration correctly inspect portable fire extinguishers and determine proper working order and placement.

## Slide 6: Enabling Objectives
The Firefighter I candidate shall correctly list in writing the proper maintenance requirements and hydrostatic testing procedures for portable fire extinguishers.
The Firefighter I candidate shall correctly identify in writing the steps for selecting the appropriate portable fire extinguisher, and demonstrate the use of extinguishers on Class A and B fires.

## Slide 7: Classes Of Fire
Five Classes of fire
  Class A: ordinary combustibles
  Class B: flammable and combustible liquids, gases, and greases
  Class C: fires that are created from electrical energy
  Class D: combustible metals and alloys
  Class K: combustible cooking oils

## Slide 8: Classes Of Fire
Class A: ordinary combustibles
  Textiles, paper, plastics, rubber, wood
Class B: flammable and combustible liquids, gases, and greases
  Alcohol, cooking oils, gasoline, LPG
Class C: fires that are created from electrical energy
Class D: combustible metals and alloys
  Lithium, magnesium, potassium, sodium
Class K: combustible cooking oils
  Vegetable and animal fats and oils

## Slide 9: Classes Of Fire
Class A: ordinary combustibles
  Water, foam, dry chemicals
Class B: flammable and combustible liquids, gases, and greases
  CO2, class B foam, dry chemical
Class C: fires that are created from electrical energy
  Eliminate the electrical energy

## Slide 10: Classes Of Fire
Class D: combustible metals and alloys
  Dry powder extinguishers
Class K: combustible cooking oils
  Wet chemical extinguishers

## Slide 11: Extinguisher Ratings
Extinguisher ratings define the extinguishing capability for each size and type of portable extinguisher.
They are rated according to the type of fire they can extinguish
The number represents their performance capability

## Slide 12: Extinguisher Ratings
Class A ratings: 1-A through 40-A
Class B ratings: 1-B through 640-B
Class C ratings: No numerical rating. Nonconductive agent
Class D ratings: No numerical rating. Tested for reactivity and toxicity
Class K ratings: Agents capable of converting fatty acids to a soap or foam. Minimum criteria extinguishes a surface area of 2.25 sq. ft.

## Slide 13: Extinguisher Ratings
Multiple markings
  Suitable for extinguishing more than one class of fire and are identified by a combination of letters

## Slide 14: Extinguisher Ratings
Class A ratings: 1-A - 1 ¼ gal (5L) of water
Class B ratings: 1-B - extinguish 1 sq. ft. of area
Class C ratings: No numerical rating

## Slide 15: Extinguisher Ratings
Class D ratings: No numerical rating.
Class K ratings: No numerical rating. Minimum criteria extinguishes a surface area of 2.25 sq. ft.

## Slide 16: Extinguisher Ratings
Pump-type water extinguishers
  Class A
Stored pressure water extinguishers
  Class A
Water-mist stored pressure extinguishers
  Class A
  Class C
Aqueous film forming foam (AFFF) extinguishers
  Class A
  Class B

## Slide 17: Extinguisher Ratings
Clean agent extinguishers
  Class A
  Class B
  Class C
Carbon dioxide extinguishers
  Class B
  Class C
Wet chemical stored-pressure extinguishers
  Class K

## Slide 18: Extinguisher Ratings
Dry chemical extinguishers
  Class A
  Class B
  Class C
  Wheeled dry chemical extinguisher

## Slide 19: Extinguisher Ratings
Dry powders
  Class D
  Class D extinguishers
  No single agent will extinguish fires in all combustible metals

## Slide 20: Extinguisher Selection
Class of burning fuel
Rating of extinguisher
Exposures to protect
Size and intensity of fire
Surrounding conditions
Ease of extinguisher handling
Personnel training

## Slide 21: Extinguisher Application
Select size and type
Check the extinguisher
  Condition of container and nozzle
  Weight
  Pressure gauge
Approach from the
windward side

## Slide 22: Extinguisher Application
PASS Method of application
  P: Pull the pin
  A: Aim the nozzle
  S: Squeeze the handles together
  S: Sweep the nozzle back and forth

## Slide 23: Extinguisher Protection
Fire extinguishers shall not be exposed to temperatures outside the listed temperature range shown on the extinguisher label
Fire extinguishers containing only water shall be protected to temperatures as low as -400F by the addition of an antifreeze that is stipulated on the fire extinguisher nameplate
NFPA 10, 2010 edition
Standard For Portable Fire Extinguishers

## Slide 24: Extinguisher Protection
Calcium chloride solutions shall not be used in stainless steel fire extinguishers

## Slide 25: Extinguisher Service &Inspection
Inspect at least once each year to ensure accessibility and operability
They must be in their designated locations
Ensure they have not been activated or tampered with
Check for physical signs of damage
Servicing is done by a fire extinguisher professional

## Slide 26: Extinguisher Inspection
Inspections
Inspect at least once each year to ensure it is accessible and in the proper location
Check nozzle or horn for obstructions or damage

## Slide 27: Extinguisher Inspection
Inspections
Check the the shell for damage
Operating instructions are legible
Check the locking pin and tamper seal are in place
Check that the extinguisher is full of agent

## Slide 28: Extinguisher Inspection
Inspections
Check that the extinguisher is full of agent
  By pressure gauge
  By weight
  By agent level
Check inspection tag
  Date of last inspection
  Maintenance
  Recharging
Examine hose and fittings

## Slide 29: Extinguisher Hydrostatic Testing
Test results should be fixed to the can
NFPA 10, 2010 edition
Standard For Portable Fire Extinguishers

## Slide 30: Obsolete Extinguishers
Inverting type fire extinguishers
  Soda-acid
  Foam
  Internal cartridge-operated water and loaded stream
  Internal cartridge dry-chemical

## Slide 31: Obsolete Extinguishers
Soft soldered or riveted copper or brass cylinders

## Slide 32: Obsolete Extinguishers
Carbon tetrachloride or chlorobromomethane
Halon
  Halon 1211
  Halon 1301

## Slide 33: Summary
Review the five classes of fire and the type of portable fire extinguisher to be used on each class of fire. Summarize the ratings and sizes of each type of extinguisher and how the ratings are determined.
Review the marking systems used on extinguishers and the various different agents used.

## Slide 34: Summary
Review inspection procedures and hydrostatic testing.
Summarize the operational methods for each fire extinguisher.